## Aug 16
NORTHERN REGIONAL LOAD DESPATCH CENTRE
OUTAGE DUE TO PLANNED SHUTDOWN AND TRIPPINGS ATTRIBUTABLE TO SELF BY LICENSEE
JAYPEE POWERGRID LIMITED
CPCC, JAMMU
LINE OUTAGE DETAILS
Month- August ,2016
|  |  | OUTAGE | RESTORATION | OUTAGE DURATION ATTRIBUTABLE TO |  |  |  | NRLDC CODE | Category Code | Reasons of Outage
CODE | EVENT NO | ELEMENT NAME | DATE & TIME | DATE & TIME | Jaypee Powergrid Limited | OTHERS | System constraints/ Natural Calamity / Militancy | Deemed Available
[5 empty] | @(T) | @(U) | & (C) | *(D)
[5 empty] | Hrs Min | Hrs Min | Hrs Min | Hrs Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
JP40004 | 48 | Jhakri Wangtu ckt II | 2016-08-06 11:20 | 2016-08-06 16:46 | 0 | 0 | 0 | 0.22639 | 357 | OSPD | Shutdown availed by KW Powerhouse for maintenance purposes.
JP40003 | 49 | Jhakri Wangtu ckt I | 2016-08-06 22:36 | 2016-08-07 05:45 | 0 | 0 | 0 | 0.29792 | 404 | LVRD | Manually opened on NRLDC instructions due to over voltage.
JP40005 | 50 | Wangtu Abdullapur ckt I | 2016-08-07 01:10 | 2016-08-07 06:27 | 0 | 0 | 0 | 0.22014 | 407 | LVRD | Manually opened on NRLDC instructions due to over voltage.
JP40003 | 51 | Jhakri Wangtu ckt I | 2016-08-07 08:46 | 2016-08-08 04:56 | 0 | 0 | 0 | 0.84028 | 424 | LVRD | Manually opened on NRLDC instructions due to over voltage.
JP40005 | 52 | Wangtu Abdullapur ckt I | 2016-08-07 09:09 | 2016-08-08 05:01 | 0 | 0 | 0 | 0.82778 | 428 | LVRD | Manually opened on NRLDC instructions due to over voltage.
JP40005 | 53 | Wangtu Abdullapur ckt I | 2016-08-24 05:48 | 2016-08-24 18:15 | 0 | 0 | 0 | 0.51875 | 1606 | LVRD | Manually opened on NRLDC instructions due to over voltage.
JP40003 | 54 | Jhakri Wangtu ckt I | 2016-08-24 06:57 | 2016-08-24 18:21 | 0 | 0 | 0 | 0.475 | 1609 | LVRD | Manually opened on NRLDC instructions due to over voltage.
JP40006 | 55 | Wangtu Abdullapur ckt II | 2016-08-24 17:41 | 2016-08-24 18:55 | 0 | 0 | 0.051389 | 0 | 1666 | LNCC | Line tripped on R - B Phase to earth fault due to heavy lightning that struck on tree in the vicinity of Span AP84-85, after patrolling the line was charged.
JP40005 | 56 | Wangtu Abdullapur ckt I | 2016-08-31 19:24 | 2016-09-01 | 0 | 0 | 0.19166 | 0 | - | LNCC | Due to incessant rain in the region, a landslide from upside hill occurred which caused a huge boulder hit the outer conductor of Y- Phase of Ckt- I between span AP275- 276, resulting into snapping of conductor , the tower span being located in the valley of the hilly terrain of this region. The snapped conductor fell on R- Phase of Ckt - I resulting into Y- Phase to R- Phase fault.
(Suresh Jain)
Sr.Vice President
JPL, Sholtu
Formulas:
Deemed Available = +[RESTORATION]-[OUTAGE]
Hrs Min = +[RESTORATION]-[OUTAGE]